## Scorecard
THE WELL PERFORMANCE RATINGTM Q2 2025
Action Area | Feature | Requirements | Verification Method 1 | Verification Method 2 | Points Available | Points Achieved | Performance Rating Notes | Documents
| PA1 Meet Thresholds for Particulate Matter | For All Spaces Except Commercial Kitchen Spaces & Industrial) Option 1: Acceptable thresholds The following thresholds are met in occupiable spaces: • PM2.5: 15 µg/m³ or lower • PM10: 50 µg/m³ or lower OR | Performance Test OR Sensor Data |  | 1
| PA1 Meet Thresholds for Particulate Matter | For All Spaces (Except Commercial Kitchen Spaces & Industrial) Option 2: Modified thresholds in polluted regions For buildings where the annual average outdoor PM2.5 level is 35 µg/m3 or higher, the following thresholds are met: PM2.5: 25 µg/m3 or lower. PM10: 50 µg/m3 or lower. | Performance Test OR Sensor Data | Technical Document (Shareable) | 1
| PA1 Meet Thresholds for Particulate Matter | For All Spaces (Except Commercial Kitchen Spaces & Industrial) For buildings where the annual average outdoor PM2.5 level is 35 µg/m3 or higher, the following thresholds are met: PM2.5 less than or equal to 30% of the 24- or 48-hour average of outdoor levels on the day(s) of performance testing. PM10 less than or equal to 30% of the 24- or 48-hour average of outdoor levels on the day(s) of performance testing. | Performance Test OR Sensor Data | Technical Document (Shareable) | 1
| PA2 Meet Enhanced Thresholds for Particulate Matter | For All Spaces The following requirement is met: a. Projects comply with the thresholds specified in the table below: 1 PM2.5: 12 µg/m³ or lower.18 1 point PM10: 30 µg/m³ or lower.19 2 PM2.5: 10 µg/m³ or lower.19 2 points PM10: 20 µg/m³ or lower.19 | Performance Test OR Sensor Data |  | 2 |  | WELL v2 projects that achieve Tier 2 achieve PA2 and are eligible for 1 Innovation feature in the WELL Performance Rating.
| PA3 Meet Thresholds for Organic Gases | For All Spaces Option 1: Laboratory-based VOC tests The following thresholds are met in occupiable spaces: • Benzene (CAS 71-43-2): 10 µg/m³ or lower • Formaldehyde (CAS 50-00-0): 50 µg/m³ or lower • Toluene (CAS 108-88-3): 300 µg/m³ or lower OR | Performance Test |  | 1
| PA3 Meet Thresholds for Organic Gases | For All Spaces Option 2: TVOC continuous monitoring The following threshold is met in occupiable spaces: • Total VOC: 500 µg/m³ or lower | Sensor Data |  | 1
Indoor Air Quality | PA4 Meet Enhanced Thresholds for Organic Gases | For All Spaces The following thresholds are met in occupiable spaces: • Acetaldehyde: 140 µg/m³ or lower • One of the following: • Acrylonitrile: 5 µg/m³ or lower • Caprolactam: 2.2 µg/m³ or lower • Benzene: 3 µg/m³ or lower • Formaldehyde: 9 µg/m³ or lower • Naphthalene: 9 µg/m³ or lower • Toluene: 300 µg/m³ or lower | Performance Test |  | 1
| PA5 Meet Thresholds for Inorganic Gases | For All Spaces Except Commercial Kitchen Spaces & Industrial The following thresholds are met in occupiable spaces: • Carbon monoxide: 10 mg/m³ [9 ppm] or lower • Ozone: 100 µg/m³ [51 ppb] or lower | Performance Test OR Sensor Data |  | 1
| PA6 Meet Enhanced Thresholds for Inorganic Gases | For All Spaces The following thresholds are met: • Carbon monoxide: 7 mg/m³ [6 ppm] or lower • Nitrogen dioxide: 40 µg/m³ [21 ppb] or lower | Performance Test OR Sensor Data |  | 1
| PA7 Ensure Adequate Ventilation | For All Spaces One of the following carbon dioxide thresholds is met in occupiable spaces: • 900 ppm or less • Not more than 500 ppm above outdoor levels | Sensor Data |  | 1
| PA8 Increase Outdoor Air Supply | For All Spaces One of the following carbon dioxide thresholds is met in occupiable spaces: • 750 ppm or less • Not more than 350 ppm above outdoor levels | Sensor Data | Tier 2 required/achieved in Option 4: Carbon dioxide measurements in WELL v2. | 1
| PA9 Meet Thresholds for Radon | For All Spaces The following threshold is met on the lowest regularly occupiable floor: • Radon: 0.15 Bq/L [4 pCi/L] or lower, as tested by a professional demonstrated not to have a conflict of interest with the WELL project. One test is conducted per 25,000 ft² of regularly occupied space at or below grade. | Sensor Data | Technical Document (Individual) | 1
Concept Total: 0
| PW1 Verify Water Quality Indicators | For All Spaces Water delivered to the project and intended for human contact (e.g., drinking, cooking and dishwashing, handwashing, showering or bathing) meets the following thresholds: • Turbidity is less than or equal to 1.0 NTU, FTU or FNU (nephelometric turbidity, formazin turbidity or formazin nephelometric units, respectively) • Coliforms are not detected in any 100 ml sample | Performance Test |  | 1
Water Quality Management | PW2 Meet Chemical Thresholds | For All Spaces The following requirements are met: • The project provides at least one drinking water dispenser, plus one drinking water dispenser per dwelling unit (if applicable). • Drinking water dispensers provide water that meets the following parameters:59 • Arsenic ≤ 0.01 mg/L. • Cadmium ≤ 0.003 mg/L. • Chromium (total) ≤ 0.05 mg/L. • Copper ≤ 2 mg/L. • Fluoride ≤ 1.5 mg/L. • Lead ≤ 0.01 mg/L. • Mercury (total) ≤ 0.006 mg/L. • Nickel ≤ 0.07 mg/L. • Nitrate ≤ 50 mg/L as Nitrate (11 mg/L as Nitrogen). • Nitrite ≤ 3 mg/L as Nitrite (0.9 mg/L as Nitrogen). • Total chlorine ≤ 5 mg/L. • Drinking water dispensers provide water that meets the following parameters:63 • Residual (free) chlorine does not exceed 4 mg/L. • The concentration of total trihalomethanes (TTHM, sum of dibromochloromethane, bromodichloromethane, chloroform and bromoform) is 0.08 mg/L or less. • The concentration of haloacetic acids (HAA5, sum of chloroacetic, dichloroacetic, trichloroacetic, bromoacetic and dibromoacetic acids) is 0.06 mg/L or less. | Performance Test |  | 1
| PW3 Meet Thresholds for Organics and Pesticides | For All Spaces The following requirements are met: a. Testing must be conducted at drinking water dispensers for at least two of the pesticides from the list below: All contaminants in the list below that are reported by the lab must comply with the following thresholds:59 • Aldrin and Dieldrin (combined): 0.00003 mg/L or less. • Atrazine: 0.1 mg/L or less. • Carbofuran: 0.007 mg/L or less. • Chlordane: 0.0002 mg/L or less. • 2,4-Dichlorophenoxyacetic acid (2,4-D): 0.03 mg/L or less. • Dichlorodiphenyltrichloroethane (DDT) and metabolites: 0.001 mg/L or less. • Lindane: 0.002 mg/L or less. • Pentachlorophenol (PCP): 0.009 mg/L or less. b. Testing must be conducted at drinking water dispensers for at least three of the organic contaminants from the list below below. All contaminants in the list below that are reported by the lab must comply with the following thresholds:59 • Benzene: 0.01 mg/L. • Benzo[a]pyrene: 0.0007 mg/L. • Carbon tetrachloride: 0.004 mg/L. • 1,2-Dichloroethane: 0.03 mg/L. • Tetrachloroethene (Tetrachloroethylene): 0.04 mg/L. • Toluene: 0.7 mg/L. • Trichloroethene (Trichloroethylene): 0.02 mg/L. • 2,4,6-Trichlorophenol: 0.2 mg/L. • Vinyl Chloride: 0.0003 mg/L. • Xylenes (o-, m- and p-): 0.5 mg/L. | Performance Test |  | 1
| PW4 Meet Thresholds for Drinking Water Taste | For All Spaces Water delivered to the project for human consumption meets the following thresholds: • Aluminum ≤ 0.2 mg/L.65 • Chloride ≤ 250 mg/L.65 • Copper ≤ 1 mg/L.65 • Manganese ≤ 0.05 mg/L. • Iron ≤ 0.3 mg/L.65 • Silver ≤ 0.1 mg/L.65 • Sodium ≤ 270 mg/L.66 • Sulfate ≤ 250 mg/L.65 • Zinc ≤ 5 mg/L.65 • Total Dissolved Solids (TDS) ≤ 500 mg/L.65 • Free Chlorine ≤ 1.25 mg/L.67 | Performance Test |  | 1
Concept Total: 0
| PL1 Provide Visual Acuity | For All Spaces Except Dwelling Units Option 1: Visual lighting design The following requirements are met: a. All indoor and outdoor spaces (including transition areas) comply with the illuminance thresholds specified in one of the following lighting reference guidelines: • IES Lighting Library, Lighting Applications Standards Collection.83 • EN 12464-1:2021 or EN 12464-2:2014.84 • ISO 8995-1:2002(E) (CIE S 008/E:2001).85 • GB50034-2013.86 • CIBSE SLL Code for Lighting.87 b. The illuminance thresholds take into consideration the tasks and the age groups of the occupants. OR | Performance Test | Technical Document (Individual) | 1
Lighting Measurements | PL1 Provide Visual Acuity | For All Spaces Except Dwelling Units Option 2: Predetermined light levels The following requirements are met: a. More than 50% of the occupants are under the age of 65. b. At least 90% of the project area is comprised of the following space types and meets the associated illuminance thresholds:88 • Offices and classrooms: minimum 30 fc at task surface. • Lobby, atrium and transition (including corridor and outdoor pathways): minimum 10 fc at floor level. • Storage spaces: minimum 10 fc at floor level. • Dining, Lounge and Restrooms: minimum 10 fc at task surface. | Performance Test | Letter of Assurance – Owner
| PL2 Meet Lighting for Day-Active People | For All Spaces Except Dwelling Units and Guest Rooms For workstations used during the daytime, electric lighting is used to achieve the following thresholds: • The following light levels are achieved for at least four hours (beginning by noon at the latest) at a height of 18 in [45 cm] above the work-plane for all workstations in regularly occupied spaces: | Performance Test |  | 2
Concept Total: 0
| PT1 Provide Acceptable Thermal Environment | For All Spaces Except Commercial Kitchen Spaces Option 1: Performance verified environmental conditions The following requirements are met, as applicable: • Mechanically conditioned regularly occupied spaces maintain thermal comfort conditions of PMV +/- 0.5 for at least 90% of occupied hours in at least 90% of regularly occupied spaces.121 | Letter of Assurance – Engineer | Performance Test, Technical Document (Shareable) | 1
Thermal Conditions | PT1 Provide Acceptable Thermal Environment | For All Spaces Except Commercial Kitchen Spaces Option 2: Long-term thermal data The following requirements are met: • Project meets Feature PM4 Monitor Thermal Environment. • Sensor data demonstrate parameters meet one of the following: 1. One of the PMV or temperature ranges described in Option 1. Dry bulb temperature may be used in place of operative temperature. Naturally conditioned projects must also measure outdoor air temperature. 2. Dry bulb temperature is between 70-77 degrees F for occupied hours. The designed air velocity is not more than 40 fpm at 5.6 ft above the floor. | Sensor Data
| PT2 Manage Relative Humidity | For All Spaces Option 1: Mechanical humidity control The following requirement is met in all regularly occupied areas, except high-humidity areas: • The mechanical system has the capability of maintaining relative humidity between 30% and 60% at all times by adding or removing moisture from the air.132,133 OR | Letter of Assurance – Engineer | Performance Test | 1
| PT2 Manage Relative Humidity | For All Spaces Option 2: Long-term humidity data The following requirements are met: • Project meets Feature PM4 Monitor Thermal Environment. • Relative humidity levels in regularly occupied areas, except high-humidity spaces, are between 30% and 60% during occupied hours. | Sensor Data
Concept Total: 0
| PS1 Limit Background Noise Levels | For All Spaces Except Dwelling Units and Guest Rooms The following requirement is met: • Background noise levels do not exceed the following thresholds, as applicable: | Performance Test |  | 2 |  | WELL v2 projects that achieve Tier 2 achieve PS1 and are eligible for 1 Innovation feature in the WELL Performance Rating.
| PS2 Achieve Sound Isolation at Walls | For All Spaces Option 1: Noise isolation class For walls that separate regularly occupied spaces the following requirements are met: • The project meets the following minimum Noise Isolation Class (NIC) or Weighted Difference Level (Dw) for each wall type, as applicable. If an interior wall meets multiple categories listed, use the highest NIC/Dw value listed. | Performance Test |  | 1
Acoustic Performance | PS2 Achieve Sound Isolation at Walls | For All Spaces Option 2: Speech privacy For walls that separate regularly occupied spaces the following requirements are met: • The sum of the measured Noise Isolation Class (NIC) or Weighted Difference Level (Dw) combined with the Noise Criteria Rating (NC) or A-weighted Sound Pressure Level (LAeq) within a room achieves the following minimum values, as applicable. If an interior wall meets multiple categories listed, use the highest value listed. | Performance Test |  | 1
| PS3 Achieve Reverberation Time Thresholds | For All Spaces Except Dwelling Units and Guest Rooms For projects in which the space types listed in the table cumulatively make up at least 10% of occupiable project area, the following requirements are met: • Reverberation time is within the ranges shown in the following table: Room Type Room Volume, v (cubic meters) Reverberation Time, t (seconds) Areas for learning v ≤ 10,000 ft3 t ≤ 0.6186 Areas for lectures 10,000 ft3 ≤ v ≤ 20,000 ft3 t ≤ 0.8203 Areas for conferencing v ≥ 20,000 ft3 t ≤ 1.0203 Areas with regularly used N/A t ≤ 1.5 PA systems Areas for dining N/A t ≤ 1.0200 Areas for fitness v ≤ 10,000 ft3 t ≤ 0.8203 10,000 ft3 ≤ v ≤ 20,000 ft3 t ≤ 1.1203 Areas for musical rehearsals v ≤ 10,000 ft3 t ≤ 1.1203 10,000 ft3 ≤ v ≤ 20,000 ft3 t ≤ 1.4203 | Performance Test | Technical Document (Individual) | 1
| PS4 Meet Thresholds for Impact Noise Rating | For All Spaces For the following room types within the project boundary the floor-ceiling construction achieves the following Normalized Impact Sound Ratings (NISR), as measured on-site, in accordance with ASTM E1007-19, ISO 16283 or equivalent, by a professional in acoustics (LnTw may be used as an equivalent metric and equivalent values may be determined by subtracting the NISR values listed below from 105): | Beta Feature Feedback Form | Technical Document (Individual) | 1 |  | WELL v2 projects that achieve Tier 2 achieve PS4 and are eligible for 1 Innovation feature in the WELL Performance Rating.
| PS5 Provide Enhanced Speech Intelligibility | For All Spaces The project meets the following requirements: •Speech enhancing telecommunication and AV accessories (e.g., active digital signal processing, noise cancellation) are provided in all rooms used for conferencing, distance learning or similar remote communications and commissioned by a professional in audio engineering. • Public address systems meet the following: - 1. Commissioned by a professional audio engineer in accordance with NFPA 72 (Annex D), BS 5839 Part 8, ISO 7240 Parts 16 and 19 or equivalent.235 - 2. Achieves a minimum STI 0.50 or CIS 0.75 is achieved in at least 50% of regularly occupied acoustically distinguishable spaces (ADS) when measured in accordance with IEC 60268-16 or equivalent.236 • Speech reinforcement systems are installed in at least 80% of classrooms and all spaces for large presentation spaces (e.g., lecture hall, conference center) and meet the following237, 238: - 1. Designed to meet audio distribution requirements in accordance with ANSI/ASA S12.60 Part 1 - 2. Commissioned by a professional accoustician or audio engineer in accordance with ANSI/INFOCOMM A102.01:2017 or equivalent. | Technical Document (Individual) |  | 1
Concept Total: 0
| PM1 Measure Air Parameters | For All Spaces except Dwelling Units The following pollutants are monitored in occupiable spaces at intervals no longer than once per year, and the results are submitted annually through the WELL digital platform. To determine the required sample locations and quantity, refer to the WELL Performance Verification Guidebook. • PM2.5. • PM10. • One of the following: • Total VOC. • Benzene, Formaldehyde, Toluene. • Carbon Monoxide. • Ozone. | On-going Data Report |  | 1
| PM2 Install Indoor Air Monitors | For All Spaces Except Dwelling Units and Guest Rooms Sensor requirements The project deploys monitors that measure at least three of the following parameters, in compliance with the requirements outlined in the Continuous Monitoring Protocols of the Performance Verification Guidebook: • PM2.5 or PM10. • Carbon dioxide. • Carbon monoxide. • Ozone. • Nitrogen dioxide. • Total VOCs. • Formaldehyde. AND | Letter of Assurance – Engineer | On-site photographs | 1
| PM2 Install Indoor Air Monitors | For All Spaces Except Dwelling Units Reporting & maintenance The following requirement is met: • Proof of calibration or replacement is submitted every three years in accordance with the requirements of the WELL Performance Verification Guidebook. | On-going Maintenance Report |  | 1
Environmental Monitoring | PM3 Promote Air Quality Awareness | For All Spaces Information about the air quality measured in PM2 Install Indoor Air Monitors is made available to occupants as follows: • Data are presented through one of the following: • Display screens prominently positioned at a height of 3.6 - 5.6 ft with at least one display per 5400 ft² of regularly occupied space. • Hosted on a website or phone application accessible to occupants. Signs are present indicating where the data may be accessed at a density of at least one sign per 5400 ft² of regularly occupied space. • Data presented include one of the following: • Concentrations of the parameters measured. • Qualitative results of air quality (e.g., colored-coded levels). | Letter of Assurance - Owner | On-site photographs | 1
| PM4 Monitor Thermal Environment | For All Spaces Thermal comfort monitors The following requirements are met: • The project monitors dry-bulb temperature and relative humidity, in compliance with the requirements outlined in the Continuous Monitoring Protocols of the Performance Verification Guidebook. • The thermal comfort data monitored is made available to occupants through one of the following: • Display screens, with at least one screen located in each 5400 ft² zone of regularly occupied space. • A website or mobile application, with at least one sign located in each 5400 ft² zone of regularly occupied space, indicating where the data may be accessed. •The thermal comfort data are updated at least once every 15 minutes. AND | On-site Photographs | Letter of Assurance – Engineer | 1
| PM5 Operable Windows | For All Spaces Part 1: Provide Operable Windows Project meets one of the below: • At least 75% of the regularly occupied spaces have operable windows that provide access to outdoor air. • For each floor, the openable window area is at least 4% the area of the indoor occupiable space.245 | Letter of Assurance – Designer | On-site Photographs
| PM5 Operable Windows | For All Spaces Part 2: Manage Window Use The following requirement is met: • Outdoor levels of PM2.5, temperature and humidity are monitored at intervals of at least once per hour, based on a data-gathering station located within 2.5 mi of the building. This monitoring system may be operated by the project or by another entity (e.g., a government). AND | Professional Narrative
| PM5 Operable Windows | For All Spaces Indicator lights and/or digital displays at windows (at least one per room with windows) cue occupants when the conditions outside are suitable for opening windows: • PM2.5: 15 µg/m³ or lower. • Dry-bulb temperature: within 15 °F of indoor air temperature setpoint. • Relative Humidity: 65% or lower. | Letter of Assurance – Engineer | On-site Photographs
| PM6 Assess and Maintain Drinking Water Quality | For All Spaces The following requirements are met: Piped water is delivered to drinking water dispensers. Water is tested quarterly in drinking water dispensers and meets the following thresholds. If any sample is found beyond these thresholds, remediation and re-testing occurs within a month: •Turbidity is 1.0 NTU, FTU or FNU or less. pH is between 6.5 and 9 (between 5.5 and 9 if a reverse osmosis system is installed at the point of use). •Total Dissolved Solids (TDS) are 500 mg/L or less. •Total Chlorine is 5 mg/L or less. •Residual (free) Chlorine is 5 mg/L or less. •Total Coliforms are not detected in a 100 ml sample. Testing is required only if residual chlorine is not detected. •Lead is 10 mg/L or less. Sampling frequency can be reduced to once per year if results are below detection limits in two consecutive samples. •Copper is 2 mg/L or less. Sampling frequency can be reduced to twice a year if results are below 0.1 mg/L in two consecutive samples; testing is no longer required if four consecutive samples are below this threshold. The number and location of sampling points for on-going monitoring complies with the requirements outlined in the Performance Verification Guidebook. For pH, use sampling locations and frequency set for residual chlorine. All test results are submitted annually through the WELL digital platform. | On-going Data Report |  | 1
Concept Total: 0
| PX1 Select Project Survey | For All Spaces Part 1: Select Project Survey Option 1: Pre-approved survey For projects with ten or more eligible employees, the following requirement is met: A survey is selected from a survey provider listed IWBI's website (https://v2.wellcertified.com/resources/preapproved-programs) OR | Policy and/or Operations Schedule |  | 1
| PX1 Select Project Survey | For All Spaces Part 1: Select Project Survey Option 2: Custom survey For projects with ten or more eligible employees, the following requirement is met: A survey is created that covers the topics listed in Appendix C1 (https://v2.wellcertified.com/en/performance-rating/appendix) | Technical Document (Shareable)
| PX1 Select Project Survey | For All Spaces Part 2: Administer Survey And Report Results Survey Administration The following requirements are met: •All eligible employees are invited to participate in the survey annually. Regular reminders are sent to eligible employees to complete the survey. •Survey protects all participant-identifying data through appropriate measures such as anonymous reporting and safe data storage. Any communication of results should be on an aggregated basis, such that no participant can be identified. •Analysis of responses is conducted by a qualified survey professional. AND | Technical Document (Shareable)
| PX1 Select Project Survey | For All Spaces Part 2: Administer Survey And Report Results Result Reporting The project or organization annually submits, through the platform, the following: Project and survey data, including: •Total number of employees invited to complete the survey and number of employees who completed the survey. •Date survey started and finished. •Project location. •Project type. •Level of WELL achievement, if applicable (e.g., WELL Certified at the Gold level under WELL v2, WELL Health-Safety Rated). •Aggregated, anonymized survey results. | On-going Data Report
| PX2 Utilize Enhanced Survey | For All Spaces Enhanced survey administration For projects with ten or more eligible employees, the following requirements are met: •Meet Feature PX1 Occupant Survey using a third-party or pre-approved survey provider. •Address at least one of the topics listed in Appendix C2 (https://v2.wellcertified.com/en/performance-rating/appendix) through a minimum of three additional survey questions utilizing a pre-approved survey provider listed on IWBI's website. AND | Technical Document (Shareable) |  | 1
Occupant Experience | PX2 Utilize Enhanced Survey | For All Spaces Result analysis and reporting The project or organization meets the following requirements: • Based on survey results, investigate correlations, inferential statistics (such as multivariate analysis), or other analyses beyond descriptive statistics. • Submit the following through the platform annually: •Aggregated, anonymized survey results for the additional topics selected. •Results of enhanced analysis. | On-going Data Report |  | 1
| PX3 Utilize Pre- and Post-Occupancy Survey | For All Spaces Pre-occupancy survey administration For projects with ten or more eligible employees, the following requirement is met: • Prior to achieving a WELL milestone, administer a survey for eligible employees using the same pre-approved survey provider(s) that will be used for Feature PX1. AND | Technical Document (Shareable) |  | 1
| PX3 Utilize Pre- and Post-Occupancy Survey | For All Spaces Result analysis and reporting The following requirements are met: • Compare results from the pre-occupancy survey against post-occupancy survey results. • Submit aggregated, anonymized pre-occupancy and post-occupancy survey results through the WELL digital platform on the following: • Aggregated, anonymized results of the pre-occupancy survey. • Comparison between the results of the pre- and post-occupancy surveys. • Total number of employees invited to complete the survey and number of employees who completed the survey. • Date pre- and post-occupancy surveys started and finished. • Location where the pre- and post-occupancy surveys were administered. • Project type. • Level of WELL achievement, if applicable. • Sociodemographic information (age and gender at minimum). | On-going Data Report
| PX4 Facilitate Interviews, Focus Groups and/or Observation | For All Spaces Administration of interviews, focus groups and/or observation The project or organization annually conducts "evaluations" (defined here as stakeholder interviews, focus groups and/or observations) that meet the following requirements: •Are conducted and analyzed by a professional experienced in qualitative research. •Comprise a culturally representative sample of the population. •Discuss the impact that the built environment and organizational initiatives have on occupant health and well-being. •Protect participant privacy and identity. AND | Technical Document (Shareable) |  | 1
| PX4 Facilitate Interviews, Focus Groups and/or Observation | For All Spaces Result analysis and reporting The following requirements are met: • Compare results from the pre-occupancy survey against post-occupancy survey results. • Submit aggregated, anonymized pre-occupancy and post-occupancy survey results through the WELL digital platform on the following: • Aggregated, anonymized results of the pre-occupancy survey. • Comparison between the results of the pre- and post-occupancy surveys. • Total number of employees invited to complete the survey and number of employees who completed the survey. • Date pre- and post-occupancy surveys started and finished. • Location where the pre- and post-occupancy surveys were administered. • Project type. • Level of WELL achievement, if applicable. • Sociodemographic information (age and gender at minimum). | On-going Data Report
| PX5 Survey for Thermal Comfort | For All Spaces A post-occupancy survey is administered at least twice a year, including once in June, July or August and once in December, January or February. For projects located in tropical regions, the survey may be administered twice a year, at least four months apart. Survey is administered at least six months after occupancy, which satisfies the following conditions: • All regular occupants are invited to participate in the anonymous survey, and responses are collected from the following number of respondents:96 | Technical Document (Audited) | Technical Document (Individual) | 2
Concept Total: 0
| PI1: Innovation I-III |  |  |  | 1
| PI2: Innovation I-III |  |  |  | 1
Innovation | PI3: Innovation I-III |  |  |  | 1
| PI4: Innovation I-III |  |  |  | 1
| PI5: Innovation I-III |  |  |  | 1
Concept Total: 0
The project achieves at least 120 EML [109 M-EDI(D65)] AND either WELL v2 Feature L05 Part 1 or L06 Part 1.
The project achieves at least 180 EML [163 M-EDI(D65)] AND either WELL v2 Feature L05 Part 1 or L06 Part 1.
At least 275 EML [250 melanopic EDI]
At least 150 EML [136 melanopic EDI]
2
2
OR
1
1
Prevailing mean outdoor temperature, tpma(out)
50 °F
92 °F
N/A
Occupant-controlled elevated air speed may be used to increase this maximum per ASHRAE 55
tpma(out) × 0.31 + 47.9 °F
tpma(out) × 0.31 + 60.5 °F
Indoor operative temperature
Notes
Minimum
Maximum
Sound Pressure Level (SPL)
Tier
Category 4:
Category 3:
Category 2:
Category 1:
Point Value
Tier
Threshold
Threshold for Projects with Enhanced Daylight
Point Value
Average SPL (Leq)
90th percentile SPL (L10)
Average SPL (Leq)
2 points
75
65
50
70
60
55
Max SPL (LMax)
1 point
1
2
50
70
60
45
65
55
45
65
55
40
66
50
45
55
35
50
60
40
dBA
dBA
dBA
dBA
dBC
dBC
Interior Wall Type
Between Loud zones and regularly occupiabied spaces.
Between areas for conferencing, learning or sleep and other regularly occupied spaces.
Between adjacent Quiet zones.
Between rooms for concentration and other regularly occupied spaces.
Between Circulation zones and regularly occupied spaces.
Minimum NIC or Dw
55
50
45
40
35
Source Room
Receiver Room
Minimum NIC + NC or Dw + LAeq
Enclosed loud zones
Open areas for concentration
Circulation zones
80
All other occupiable areas
85
Enclosed areas for conferencing
Enclosed areas for learning
Enclosed areas for sleeping
Open areas for concentration
Enclosed quiet zones
Enclosed areas for conferencing
75
80
85
Areas for music rehearsal
v ≤ 10,000 ft3
10,000 ft3 ≤ v ≤ 20,000 ft3
t ≤ 1.1203
1.0 ≤ t ≤ 1.4203
Room Type
Location of Applicable Floor-Ceiling Assembly
Tier 1
1 point
Minimum NISR208
Tier 2
2 points
Minimum NISR208
Quiet zones (except areas for concentration)
Above
52
57
Areas for fitness
Below
47
52
Enclosed areas for concentration and conferencing
Above
47
52
Open areas for concentration
Areas for retail and dining
Above
Below
42
42
47
47
Number of regular occupants
More than 45
20 to 45
Less than 20
80% of those regular occupants
15 regular occupants
35% of those regular occupants
Minimum number of responses
The survey includes an assessment of overall satisfaction with thermal performance and identifies thermal comfort-related issues in accordance with either: •The sample survey in Appendix T1 in WELL v2. •Any survey from the “Features C04 and C05: Approved third-party surveys” section on IWBI's website (https://v2.wellcertified.com/resources/preapproved-programs). The results of the survey responses comply with one of the target satisfaction thresholds, as specified in the table below:
Tier
1
2
Thermal Comfort Satisfaction Thresholds
80% of regular occupants
90% of regular occupants
Point Value
1
2
Circulation zones
Enclosed areas for learning
Enclosed areas for sleeping
Enclosed client zones
Open areas for concentration
Circulation zones
70
Enclosed quiet zones
75
Enclosed areas for conferencing
Enclosed areas for learning
Enclosed areas for sleeping
80
Tier
Particulate Matter Threshold
Point Value
OR